EQUIPMENT DATA SHEET Tranter GmbH ¦ Horizontal Spiral Heat Exchanger ¦ S-2858/2.16

DESCRIPTION

Tranter GmbH horizontal spiral heat exchanger, all-carbon-steel construction, ASME Section VIII Division 1 stamped and certified. Built new in 2014/2015 for Shell Canada Energy's Carmon Creek Project (Alberta) as a produced water trim cooler (Tag No. 2120-E-40480). Heat transfer area 184.0 m² (1,980 ft²). Rated for sour gas service per NACE MR0175 / ISO 15156. Unit is unused; shipping crate has been opened.

1. IDENTIFICATION & REGISTRATION

| Manufacturer | Tranter GmbH, Hohe-Flum-Str. 31, D-79650 Schopfheim, Germany |
| --- | --- |
| Manufacturer Serial No. | S-2858/2.16 |
| Tranter Order No. | W 2858/2 |
| Equipment / Tag No. | 2120-E-40480 |
| Shell Canada PO No. | 4511879514 |
| Project | Carmon Creek Project — Produced Water Trim Cooler |
| Year Built | 2014/2015 |
| CRN (Canadian Reg. No.) | W5688.2 |
| National Board No. | 238 |
| ASME U Cert. of Auth. No. | 33,586 (Tranter GmbH) |
| Third-Party Inspector / Comm. | TÜV Thüringen e.V., Essen — N.B. 14863 A (inspected April 1, 2015) |
| Drawing No. | S-2858/2 Rev. 03, page 1/6 |
| HS Code | 84195000 |

2. DESIGN DATA

| Equipment Type | Horizontal Spiral Heat Exchanger |
| --- | --- |
| Design Code | ASME Section VIII, Division 1 — Ed. 2010 / Addenda 2011a |
| Heat Transfer Area | 184.0 m² (1,980 ft²) |
| Shell OD | 1,800 mm (70.9 in.) |
| Chamber Length (each) | 2,003 mm (78.9 in.) |
| MAWP — Chamber I (Shell) | 24.5 barg (355 psig) at 200 °C (392 °F) |
| MAWP — Chamber II (Coil) | 24.5 barg (355 psig) at 200 °C (392 °F) |
| MAEWP — Both Chambers | 1 barg (14.5 psig) at 200 °C (392 °F) |
| MDMT — Both Chambers | −45 °C (−49 °F) at 24.5 barg |
| Hydrostatic Test Pressure | 36.11 barg (524 psig) |
| Impact Testing | Yes — all major components tested at −45 °C |
| Sour Service Compliance | NACE MR0175 / ISO 15156 (2nd ed., 2009-10-15) |
| Stress Relieved | No |
| X-Ray | Spot |
| Ultrasonic | Spot |

3. MATERIALS OF CONSTRUCTION

| Shell / Body Plate | SA-516 Grade 70N (normalized), 30 mm — P-1, Group 2 |
| --- | --- |
| Divider Sheets | SA-516 Grade 70N, 30 mm — P-1, Group 2 |
| Covers | SA-516 Grade 70N, 110 mm — P-1, Group 2 |
| Nozzle Pipe | SA-333 Grade 6 (low-temp carbon steel) — P-1, Group 1 |
| Nozzle Flanges | SA-350 LF2 Cl.1 (low-temp carbon steel) — P-1, Group 2 |
| Stud Bolts | SA-320 L7M — 1¾" 8UN × 15½" (68 off) |
| Nuts | SA-194 7M |
| Corrosion Allowance | 1.5 mm (all pressure parts) |

4. NOZZLE SCHEDULE

| N1 | 8" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |
| --- | --- |
| N2 | 8" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange (half-pipe attached to shell) |
| N3 | 6" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange (half-pipe attached to shell) |
| N4 | 6" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |
| N5 | 2" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |
| N6 | 2" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |
| N7 | 2" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |
| N8 | 2" 300# WN/RF — SA-333 Gr.6 pipe / SA-350 LF2-Cl.1 flange |

5. PHYSICAL & SHIPPING DATA

| Supports | 2 lifting lugs + saddle, welded to shell |
| --- | --- |
| Crated Dimensions (L × W × H) | 360 cm × 255 cm × 298 cm (142" × 100" × 117") |
| Net Weight | 27,260 kg (60,100 lbs) |
| Gross (Crated) Weight | 29,475 kg (64,980 lbs) |
| Condition | New, unused — crate open (inspected) |

Sources: ASME Form U-1 (data book), data plate photograph, packing list, leakage test certificate, Certificate of Compliance — Tranter GmbH Final Data Book, Serial No. S-2858/2.16 (2120-E-40480), 2014/2015.  P-number assignments per ASME BPVC Section IX, Table QW/QB-422.